GOVERNMENT OF TAMIL NADU

ELECTRICAL INSPECTORATE

E-mail:eivlr@tn.gov.in								Visit: www.tnei.tn.gov.in

[Reply by Designation Only]

From Er.G.Purushothaman, M.E., Assistant Electrical Inspector, Office of the Electrical Inspector, No.19, 1st Floor, 10th East Main Road, Gandhi Nagar East, Vellore-632 006.

Order No : VLR {{Letter_No}}/AEI/VLR/R 32/2026, Dated: {{Report_date}}

To

M/s. {{Consumer_Address}}

Whereas the installation at the above  was inspected on {{Inspection_date}}, under Regulation 32 of Central Electricity Authority (Measures relating to Safety and Electric Supply) Regulations, 2023, for the year 2026-2027 and whereas it appears to me that you have not complied with the CEA (MSES) Regulations, 2023 in the following respects as detailed below. You are hereby called upon to comply with the said Regulations on or before {{RR_date}}  and to report compliance in writing to Electrical Inspector office, Vellore with a copy to the Chief Electrical Inspector to Government, Chennai 32.

An appeal may be filed against this order under sub section 2 of section 162 of The Electricity Act, 2003 within three months of the date on which this order is served or delivered or is deemed to have been served but this order must be complied with not withstanding such appeal, unless the appellate authority (namely, the Chief  Electrical Inspector to Government, Chennai) on or before the date specified in paragraph I above suspends its operation.

DEFECTS

- Following defects were noticed in consumer DP structure and {{Tfr_kVA}} kVA Transformer yard:

A) Adequate Lighting arrangement in a permanent standard manner should be provided for the DP structure yard.							          	    	    	R 14(1)

B) The weeds and grass grown inside the DP Structure yard should be removed and the yard kept neat and tidy.  										R 14(1)

C) The earth electrodes meant for DP structure, {{Tfr_kVA}} kVA Transformer Neutral and Body earth should be identified and covered with suitable cover slabs.				        	R 14(1)

D) The metal parts of the DP structure are found rusted. The same should be cleaned and painted with anti-corrosive paint.							          		R 14(1)

E) The operating handle and down rod of the AB switch is not connected with earth. The AB switch-operating handle  should be connected to earth effectively using braided or flexible earth lead.   R 14(1)

F) The breather unit is not found fixed in  {{Tfr_kVA}} kVA Transformer. The new breather unit filled with fresh silica gel and oil cup filled with oil upto level marking should be provided.	R 14(1)

G) The off load tap changer of Transformer found not locked. The same should be kept under locked to avoid unauthorized operations.					       		R 14(1)

H) Rusted Metal part of DP structure yard gate and fencing should be painted and it should be connected to earth effectively.							       R 14(1)&R50(1)

I) The metallic portion on the either side of the gasket in the cable adaptor box on the 
secondary side of the transformer should be interconnected using suitable “U” clamps effectively to ensure continuity of earth.								R43(viii)

- A copy of building plan approval obtained from local body and permit letter for building blocks should be sent for reference.									R 14(1)

- A Protection class CT having suitable ratio should be provided in the neutral earthing circuit of Transformer and connected to the Earth fault relay to trip the secondary control of ACB at Main MV panel in the event of any earth fault / leakage.						R 47(2)(ii)

- Cable route indicators should be provided at regular intervals along the route of the cable between main MV Panel room to various building blocks in a permanent standard manner. 	      R 14(1)

- The front cover of the feeder controls at the MV panel and switch boards should be affixed with suitable labeling showing the name of the circuit, size of the feeder and the rating of fuses /setting of controls to be adopted, in a permanent manner.  			  	          	   R 14(1) & R 21(6)

- The cable trench inside the MV panel room is kept open. The same should be covered using suitable non  inflammable cover slabs.								R 14(1)

- In MV panel, and SSB panels some of removed meter spaces found open. Panel front holes/unused ways  should be closed properly with insulating sheets or dummy.			R 14(1)

- The new electrically tested rubber mats conforming to IS 15652 - 2006 standards should be provided in front of Main MV panel, SSBs, PDBs panel to its full length.				R 21(5)

- Adequate number of Fire Extinguishers confirming to the relevant standards should be provided in Main MV panel room, DG set area and in all PDB rooms. It should be maintained, periodically inspected and tested as per standards.  			               		             R 29(1)(2)

- Adequate rating of 30 mA RCBO should be provided on the incoming side of LDBs and PDBs which are feeding the plug points, Lab equiments feeding from Power plug sockets and portable equipments etc.,											R 44

- Earth electrodes of Admin block, lightning arrestor are not traceable. Adequate number of Earth electrodes for the Electrical installations should be provided with 45 x 45 cms masonry earth troughs and covered using RCC slabs.								R 14(1)

- The cable glands of incoming and outgoing cables in Main MV panel, MLDB, APFC, PDB and LDB panels should be connected to earth with suitable earth clips.				 R 39(ii)

- Circuit list is not affixed inside the front cover of all MCB DB’s. A clear circuit list with load details, size of the cable, circuit number, rating of MCB should be affixed conspicuously inside the front cover of the all PDBs and LDBs.							          	R21(6)

- Suitable metal barricade arrangement should be provided in front of the sub panels erected in various blocks maintaining required front and side clearances.				R 14(1), R39(iii)

- The motor of every equipment and their respective control switch, starter, emergency ON/OFF switch etc., are not identified with proper circuit number. Each of the above should be identified permanently as shown in approved drawings for easy identification.					R 14(1)

- Earth flat of building lightning arrestor found cut. Same should be changed and connected to earth electrode effectively and continuity to be checked periodically. Adequate number of conventional type lightning protection  system conforming to IS/IEC 62305 standards should be provided for covering the entire college premises from direct lightning strokes.			       R14(1) & R77

- A) The flexible supply cables for lighting circuits and AC outdoor units  found laid in PVC conduits. All the PVC conduits laid in the college premises for PDB and lighting wiring should be replaced by earthed metal conduits. 									R 39(i)(ii)

B) The flexible wire joints in class rooms and labs should be avoided and all the electrical fittings should be inaccessible to the students. All wirings should be protected suitable casings to avoid mechanical damages.								     R14(1), R39(i)(ii)

- Danger Notice boards are not found affixed on PDB and LDBs. A Standard Danger Notice boards with working voltage should be affixed on the Transformer yard gate , control panel doors of  all motors, Main MV Panel, APFC panels, SSBs, all PDBs and all LDBs.   		            	R 20

- Some of the CNC Machines in Labs, panels in new building blocks found under erection. Necessary Permission under regulation 45 of CEA (MSES) Regulations, 2023 should be obtained for the above said installations. 										R 45

- The following should be connected to the earth effectively

- Metal parts of all Street light poles

- All AC outdoor units

- Metal parts of all machineries in Electrical and Mechanical Laboratories

- Metallic cable glands of supply cables at all the cable terminations.

- Metallic cable trays in which the supply cables are taken.

- Mounting base plate on which the controls mounted on LT switch boards/panels.

- Sheet metal works covering the supply leads.		           R 39(ii),R43(vii)(viii)

- The Periodical tests are not done.

a.	Transformer oil        -     for dielectric strength and acidity.

b.	Earth electrodes       -     for individual and combined values of resistance to earth.

c.	Relays 		        - 	  for sensitivity to correct functioning

All the above tests should be carried out and the results should be recorded and maintained in a log-book.   					       		  R14(1) & R48(5)(6)

- There is no supervisor to look after the HV and MV installations. A person holding valid SCC issued by Tamil Nadu  Electrical Licensing Board should be appointed and the copy of his posting orders and consent letter sent to this Electrical Inspector office early. 				            		R 3(1)(2)

Earthed cradle type guarding should be provided for the incoming OH lines in consultation with TANGEDCO authorities.							      	           	R 76

- Adequate Lighting arrangement in a permanent standard manner should be provided for the DP structure yard.							          	    	 	R 14(1)

- The weeds and grass grown inside the DP Structure yard should be removed and the yard kept neat and tidy.  										       	R 14(1)

- The earth electrodes meant for DP structure, {{Tfr_kVA}} kVA Transformer Neutral and Body earth should be identified and covered with suitable cover slabs.				R 14(1)

- The metal parts of the DP structure are found rusted. The same should be cleaned and painted with anti-corrosive paint.							          		R 14(1)

- The operating handle of AB switch is found not locked. It should be locked properly to avoid un authorized operation. 	         								R 14(1)

- The silica gel in the breather unit of the {{Tfr_kVA}} kVA Transformer turned pink in colour. It should be replaced by fresh silica gel.							R14(1)

- The metallic portion on the either side of the gasket in the cable adaptor box on the primary and
secondary side of the transformer should be interconnected using suitable “U” clamps effectively to ensure continuity of earth.									R43(viii)

- Cable route indicators should be provided at regular intervals along the route of the cable between DP structure at the point of supply to the Transformer in permanent manner. 	      	        	R 14(1)

- The front cover of the feeder controls at the MV panel and switch boards should be affixed with suitable labeling showing the name of the circuit, size of the feeder and the rating of fuses /setting of controls to be adopted, in a permanent manner.  			  	              R 14(1) & R 21(6)

- The new electrically tested rubber mats conforming to IS 15652 - 2006 standards should be provided in front of Main MV panel , SSB1, MCC 1 panel to its full length.			R 21(5)

- The incoming supply indication lamps in main MV panels found failed. The same should be replaced with new one and live supply indication and breaker on/ off status identifications should be marked.												       	R 14 (1)

- Adequate number of Fire Extinguishers confirming to the relevant standards should be provided in Main MV panel room, DG set area and in all PDB rooms. It should be maintained, periodically inspected and tested as per standards.  			               		             R 29(1)(2)

- The earth electrodes meant for {{DG_kVA}} kVA DG sets and Lightning arrestors should be identified on the inner side of walls of the earth troughs.				             R 14(1)

- The bolt and nuts connecting {{DG_kVA}}  kVA DG set body and neutral earth electrodes found rusted. Rusted bolt and nuts in all earth electrodes should be replaced with new one.	 R 14(1)

- Adequate rating of 30 mA RCBO should be provided on the incoming side of LDBs and PDBs which are feeding the plug points, portable equipments etc.,					R 44

- The cable glands of incoming and outgoing cables in Main MV panel and MLDB panel should be connected to earth with suitable earth clips.						R 39(ii)

- Circuit list is not affixed inside the front cover of all MCB DB’s. A clear circuit list with load details, size of the cable, circuit number, rating of MCB should be affixed conspicuously inside the front cover of all the PDBs and LDBs. 							R 21(6)

- The motor of every equipment and their respective control switch, starter, emergency ON/OFF switch etc., are not identified with proper circuit number. Each of the above should be identified permanently as shown in approved drawings for easy identification.			R 14(1)

- Adequate number of conventional type lightning arrestors conforming to IS/IEC 62305 standards should be provided for covering the entire premises from direct lightning strokes.      R14(1) & R77

- The flexible supply cables on incoming and outgoing side of UPS units found laid in PVC conduits. All the PVC conduits laid inside the premises for PDB and lighting wiring should be replaced by earthed metal conduits. 							    	R 39(i)(ii)

- Danger Notice boards are not found affixed on PDB and LDBs. A Standard Danger Notice boards with working voltage should be affixed on the Transformer yard gate , control panel doors of  all motors, Main MV Panel, APFC panels, MCCs, all PDBs and all LDBs.   		R 20

- The offline energy meter provided at the control panel of  the {{DG_kVA}} kVA DG set  should be calibrated regularly at Government Electrical Standards Laboratory once in three years.	   R 14(1)

- The  {{DG_kVA}} kVA DG sets in the installations were not yet re-registered under Tamil Nadu Tax on generation and consumption or Sale of Electricity Act & Rules 2003. The same should be got registered early By submitting form  A – 1 along with treasury challan in original for Rs. 2000 /= for each generator.				       Rule 5 of TN Tax on generation and consumption or Sale of Electricity Act  2003

- The earth electrodes meant for {{DG_kVA}} kVA DG sets and Lightning arrestors should be identified on the inner side of walls of the earth troughs.				            R 14(1)

The Electricity Tax for the consumption of energy generated by the DG sets should be paid regularly and receipted challan along with monthly return in form C2 should be sent to this office.	    Rule 54 of  Tamil Nadu tax on Generation  and consumption or sale of electricity Rules,2003

- The following should be connected to the earth effectively

- Metallic cable glands of supply cables at all the cable terminations.

- Metallic cable trays in which the supply cables are taken.

- Mounting base plate on which the controls mounted on LT switch boards/panels.

- Sheet metal works covering the supply leads.		           R 39(ii),R43(vii)(viii)

- The Periodical tests are not done.

a.	Transformer oil        -     for dielectric strength and acidity.

b.	Earth electrodes       -     for individual and combined values of resistance to earth.

c.	Relays 		        - 	  for sensitivity to correct functioning

All the above tests should be carried out and the results should be recorded and maintained in a log-book.   					       		  R14(1) & R48(5)(6)

23.

24.

All the above defects should be rectified as per the provisions of Regulation – 31(1) of CEA (MSES) Regulations, 2023.

|  | Assistant Electrical Inspector / Vellore |
| --- | --- |

Copy Submitted to : The Chief Electrical Inspector to Govt., Chennai.

Copy Submitted to : The Electrical Inspector, Vellore.

DETAILS OF INSTALLATIONS

| 01 | Transformers | 1 x {{Tfr_kVA}} kVA, 11 kV/433 V |
| --- | --- | --- |
| 02 | Generator | 1 x {{DG_kVA}} kVA, 415 V |
| 03 | Equipments upto and inclusive of 250 V | {{No_of_250V}} Nos + Power sockets |
| 04 | Equipments above 250 V and upto and inclusive of 650 V | {{No_of_250_650V_Equip}} Nos. |
| 05 | Equipments above 650 V | {{Equipments_above_650V}} Nos. |
| 06 | Total Power Load | {{Power_Load}} |
| 07 | Lighting Load | {{LL_load_in_kW}} kW |
| 08 | a) Authorized Person | Thiru. {{C_license_person}}, holding C- {{C_lic_No}} valid upto {{C_lic_validity}} |
|  | b) Safety officer | Nil. |
| 09 | Inspection fees | Advance fees paid: Rs. {{Paid_fees}}/- Ch. No : {{Challan_No}} Dated: {{paid_date}} DTO/Vellore Billed for Rs. {{Billed_amt}} /- Excess/Balance : Rs. {{Excess_Balance_Amount}} /- |
| 10 | Supplier’s side defects | Nil |
| 11 | Unauthorized Loads | Nil |
| 12 | Testing and Maintenance | Due / Done |
| 13 | Date of Commissioning of Installation | {{DSC}} |
| 14 | HT S.C No with TANGEDCO particulars | H.TS.C. No: {{HTSC_NO}} / SE VEDC TVMEDC TEDC / Vellore Thiruvannamalai Thirupathur Sanctioned Demand – {{Sanct_Demand}} KVA |
| 15 | Compliance of last Regulation 32 inspection defects - Partly complied. Also Vide D/R. |  |